MNG 180-12

12V180AH

MNG Series GEL Battery

VRLA Battery

MNG Series-- Storage-type Gelled Battery

- completely sealed and maintenance-free, low self-discharge

- 100% precise quality testing, stable quality and high reliable performance

- Unique grid alloy formula, Gelled electrolyte formula and updated manufacturing technique

- Floating & standby use:up to 12 years

- Cycle use 1: More than 350 cycles at 100% DOD

- Cycle use2: More than 1800cycles at 30% DOD

Application:

- Telecommunications

- UPS/EPS

- DC PowerSupply

- Solar system

- Wind Power System

- Auto Control Sytem

Construction:

- Component ......Raw material

- Positive ........Lead dioxide

- Negative ........Lead

- Container ........ABS

- Cover ........ABS

- Sealant ........Epoxy

- Safety valve .... Rubber

- Terminal ........Copper/Pb

- Separator ........Fiber glass

- Electrolyte ....... Gelled acid

B5 Terminal

T16 Terminal

Speification:

| Battery Model | MM 180-12 12V180AH |  |  |  |
| --- | --- | --- | --- | --- |
| Designed Floating Life | Up to 12 Years |  |  |  |
| Capacity (25℃) | 20HR(9.0A,10.8V) | 10HR(18A,10.8V) | 5HR(31.5A,10.8V) | 1HR(108A,10.5V) |
|  | 180AH | 173AH | 153AH | 108AH |
| Dimensions | Length | Width | Height | Total Height |
|  | 523mm (20.59inch) | 240mm (9.45inch) | 220mm (8.66inch) | 245mm (9.64inch) |
| Approx. Weight | 55.50Kg (123 lbs) |  |  |  |
| Internal Resistance | Full charged at 25℃:≤3.0mΩ |  |  |  |
| Self Discharge | 2% of capacity declined per month at (25℃) |  |  |  |
| Capacity Affected by Temp.(20HR) | 40℃ | 25℃ | 0℃ | -15℃ |
|  | 102% | 100% | 85% | 65% |
| Charge Voltage(25℃) | Cycle use |  | Float use |  |
|  | 14.4-14.6V(-30mV/℃), max. Current:60A |  | 13.6-13.8V (-20mV/℃) |  |

VRLA Battery

MNG 180-12

12V180AH

Terminal Voltage (V) and Discharge Time

Capacity Retention Characteristic

Battery Vlotage and Charge Time for Standby Use

Battery Vlotage and Charge Time for Cycle Use

Tickle(or Float) Service Life

Cycle Service Life

Battery Vlotage and Charge Time for Cycle Use

| Constant Current Discharge(CC,Unit:A) at 25℃(77℉) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| F.V/Time | 5Min | 10Min | 15Min | 30Min | 1Hr | 2Hr | 3Hr | 4Hr | 5Hr | 8Hr | 10Hr | 20Hr |
| 9.60V | 576 | 378 | 306 | 205 | 108 | 63 | 46.3 | 36 | 30.6 | 21.1 | 18.9 | 10.1 |
| 10.2V | 558 | 342 | 288 | 196 | 101 | 60 | 45 | 35 | 29 | 20.5 | 18.5 | 9.9 |
| 10.5V | 540 | 306 | 252 | 184 | 98 | 58.5 | 44 | 34.5 | 28.5 | 20.3 | 18.2 | 9.7 |
| 10.8V | 518 | 288 | 234 | 169 | 94.5 | 57 | 42.5 | 34 | 28 | 19.8 | 18 | 9.5 |
| 11.1V | 503 | 270 | 216 | 151 | 92 | 55.5 | 41.4 | 33 | 27.4 | 19.3 | 17.1 | 9 |
| Constant Power Discharge (CP,Unit:W) at 25℃(77℉) |  |  |  |  |  |  |  |  |  |  |  |  |
| F.V/Time | 5Min | 10Min | 15Min | 30Min | 1Hr | 2Hr | 3Hr | 4Hr | 5Hr | 8Hr | 10Hr | 20Hr |
| 9.60V | 5932 | 3893 | 3151 | 2152 | 1134 | 661 | 486 | 378 | 321 | 221 | 198 | 106 |
| 10.2V | 5747 | 3522 | 2966 | 2058 | 1060 | 630 | 471 | 367 | 304 | 215 | 194 | 104 |
| 10.5V | 55624 | 3151 | 2595 | 1932 | 1029 | 614 | 462 | 362 | 299 | 213 | 191 | 101 |
| 10.8V | 5335 | 2966 | 2410 | 1774 | 992 | 598 | 446 | 357 | 294 | 207 | 189 | 99.5 |
| 11.1V | 5180 | 2781 | 2224 | 1585 | 966 | 582 | 434 | 346 | 287 | 202 | 179 | 94 |