NP 33-12

12V33AH

VRLA Battery

VRLA Battery

- completely sealed and maintenance-free, low self-discharge

- 100% precise quality testing, stable quality and high reliable performance

- Unique grid alloy formula and updated manufacturing technique

- Floating & standby use:up to 5 years

- Cycle use 1: More than 280 cycles at 100% DOD

- Cycle use2: More than 1400cycles at 30% DOD

Application:

- Telecommunications

- UPS/EPS

- DC Power Supply

- Solar system

- Wind Power System

- Auto Control System

Construction:

- Component ......Raw material

- Positive ........Lead dioxide

- Negative ........Lead

- Container ........ABS

- Cover ........ABS

- Sealant ........Epoxy

- Safety valve ....Rubber

- Terminal ........Copper/Pb

- Separator ........Fiber glass

- Electrolyte .......Sulfuric acid

B4 Terminal

T11 Terminal

Specification:

| Battery Model | NP 33-12 12V33AH |  |  |  |
| --- | --- | --- | --- | --- |
| Designer Floating Life | Up to 5 Years |  |  |  |
| Capacity (25℃) | 20HR(1.66A,10.5V) | 10HR(3.30A,10.5V) | 5HR(5.61A,10.5V) | 1HR(18.2A,10.5V) |
|  | 33.20AH | 33.00AH | 28.05AH | 18.20AH |
| Dimensions | Length | Width | Height | Total Height |
|  | 196mm (7.72inch) | 130mm (5.1inch) | 155mm (6.10inch) | 180mm (6.69inch) |
| Approx. Weight | 10.80Kg (23.81 lbs)±5% |  |  |  |
| Internal Resistance | Full charged at 25℃:≤9.0mΩ |  |  |  |
| Self Discharge | 2% of capacity declined per month at (25℃) |  |  |  |
| Capacity Affected by Temp.(20HR) | 40℃ | 25℃ | 0℃ | -15℃ |
|  | 102% | 100% | 85% | 65% |
| Charge Voltage(25℃) | Cycle use |  | Float use |  |
|  | 14.40-15.00V(-30mV/℃), max. Current:8.25A |  | 13.50-13.80V (-20mV/℃) |  |

12V100AH

VRLA Battery

NP 33-12

12V33AH

Terminal Voltage (V) and Discharge Time

Capacity Retention Characteristic

Battery Vlotage and Charge Time for Standby Use

Battery Vlotage and Charge Time for Cycle Use

Tickle(or Float) Service Life

Cycle Service Life

Battery Vlotage and Charge Time for Cycle Use

| Constant Current Discharge(CC,Unit:A) at 25℃(77℉) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| F.V/Time | 5Min | 10Min | 15Min | 30Min | 1Hr | 2Hr | 3Hr | 4Hr | 5Hr | 6Hr | 10Hr | 20Hr |
| 1.85V/Cell | 73.8 | 54.3 | 47.2 | 28.5 | 16.8 | 9.9 | 7.4 | 6.21 | 5.11 | 4.70 | 3.13 | 1.61 |
| 1.80V/Cell | 76.6 | 56.4 | 49.0 | 29.5 | 17.5 | 10.3 | 7.7 | 6.46 | 5.32 | 4.90 | 3.27 | 1.63 |
| 1.75V/Cell | 84.3 | 59.2 | 51.4 | 30.7 | 18.2 | 10.6 | 7.9 | 6.53 | 5.38 | 4.95 | 3.30 | 1.66 |
| 1.70V/Cell | 94.2 | 62.1 | 53.9 | 32.2 | 18.5 | 10.8 | 8.1 | 6.59 | 5.43 | 5.00 | 3.33 | 1.71 |
| 1.67V/Cell | 104.2 | 64.9 | 56.3 | 33.1 | 19.2 | 11.1 | 8.3 | 6.66 | 5.48 | 5.04 | 3.36 | 1.73 |
| Constant Power Discharge (CP,Unit:W) at 25℃(77℉) |  |  |  |  |  |  |  |  |  |  |  |  |
| F.V/Time | 5Min | 10Min | 15Min | 30Min | 1Hr | 2Hr | 3Hr | 4Hr | 5Hr | 6Hr | 10Hr | 20Hr |
| 1.85V/Cell | 140.2 | 103.3 | 89.6 | 54.1 | 31.9 | 18.8 | 14.0 | 11.79 | 9.71 | 8.93 | 5.96 | 3.06 |
| 1.80V/Cell | 145.5 | 107.2 | 93.1 | 56.1 | 33.2 | 19.5 | 14.6 | 12.28 | 10.11 | 9.31 | 6.20 | 3.19 |
| 1.75V/Cell | 160.1 | 112.6 | 97.7 | 58.4 | 34.5 | 20.1 | 15.0 | 12.41 | 10.21 | 9.40 | 6.27 | 3.23 |
| 1.70V/Cell | 179.0 | 117.9 | 102.4 | 61.2 | 35.2 | 20.5 | 15.3 | 12.53 | 10.31 | 9.49 | 6.33 | 3.26 |
| 1.67V/Cell | 197.9 | 123.3 | 107.0 | 62.9 | 36.5 | 21.1 | 15.7 | 12.65 | 10.42 | 9.58 | 6.39 | 3.29 |